## Sheet1
start
checkAction |  | previous | succes
success/falure | failure | checkUndo | succes/failure
success |  |  | failure
next |  |  | ABORT
checkLast
last
COMPLETE

## Sheet2
| Success-forward | Success-reverse | Failure-forward | Failure-reverse
SCENARIO_STARTED | FIND_CHILLER_TO_TURN_ON_SUCCESS
SCENARIO_RECOVERED
SCENARIO_ABORTED
EQUIPMENT_NOT_AVAILABLE
SCENARIO_COMPLETED
FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS
FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_PRIMARY_VARIABLE_PUMP_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS
FIND_PRIMARY_VARIABLE_PUMP_TO_TURN_ON_SUCCESS | FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS | FIND_PRIMARY_VARIABLE_PUMP_TO_TURN_ON_SUCCESS
FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS
FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS
FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | FIND_CT_FAN_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS
FIND_CT_FAN_TO_TURN_ON_SUCCESS | FIND_CT_VARIABLE_FAN_TO_TURN_ON_SUCCESS | FIND_CT_FAN_TO_TURN_ON_SUCCESS
FIND_CT_VARIABLE_FAN_TO_TURN_ON_SUCCESS | FIND_HEADER_TO_TURN_ON_SUCCESS | FIND_CT_VARIABLE_FAN_TO_TURN_ON_SUCCESS
FIND_HEADER_TO_TURN_ON_SUCCESS | CHILLER_TURN_ON_REQUESTED | FIND_HEADER_TO_TURN_ON_SUCCESS
CHILLER_TURN_ON_REQUESTED |  | CHILLER_TURN_ON_REQUESTED
PRIMARY_PUMP_TURN_ON_REQUESTED |  | PRIMARY_PUMP_TURN_ON_REQUESTED
PRIMARY_VARIABLE_PUMP_TURN_ON_REQUESTED
SECONDARY_PUMP_TURN_ON_REQUESTED
CONDENSER_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_ON_REQUESTED
COOLING_TOWER_TURN_ON_REQUESTED | PRIMARY_VARIABLE_PUMP_TURN_ON_REQUESTED
CT_FAN_TURN_ON_REQUESTED | SECONDARY_PUMP_TURN_ON_REQUESTED
CT_VARIABLE_FAN_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_ON_REQUESTED
HEADER_TURN_ON_REQUESTED | COOLING_TOWER_TURN_ON_REQUESTED
CHILLER_TURN_OFF_REQUESTED | CT_FAN_TURN_ON_REQUESTED
PRIMARY_PUMP_TURN_OFF_REQUESTED | CT_VARIABLE_FAN_TURN_ON_REQUESTED
PRIMARY_VARIABLE_PUMP_TURN_OFF_REQUESTED | HEADER_TURN_ON_REQUESTED
SECONDARY_PUMP_TURN_OFF_REQUESTED | CHILLER_TURN_OFF_REQUESTED
CONDENSER_PUMP_TURN_OFF_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED
COOLING_TOWER_TURN_OFF_REQUESTED | PRIMARY_VARIABLE_PUMP_TURN_OFF_REQUESTED
CT_FAN_TURN_OFF_REQUESTED
CT_VARIABLE_FAN_TURN_OFF_REQUESTED
HEADER_TURN_OFF_REQUESTED
CHILLER_TURNED_ON
PRIMARY_PUMP_TURNED_ON
PRIMARY_VARIABLE_PUMP_TURNED_ON
SECONDARY_PUMP_TURNED_ON
CONDENSER_PUMP_TURNED_ON
COOLING_TOWER_TURNED_ON
CT_FAN_TURNED_ON
CT_VARIABLE_FAN_TURNED_ON
HEADER_TURNED_ON
CHILLER_TURNED_OFF
PRIMARY_PUMP_TURNED_OFF
PRIMARY_VARIABLE_PUMP_TURNED_OFF
SECONDARY_PUMP_TURNED_OFF
CONDENSER_PUMP_TURNED_OFF
COOLING_TOWER_TURNED_OFF
CT_FAN_TURNED_OFF
CT_VARIABLE_FAN_TURNED_OFF
HEADER_TURNED_OFF
VALVE_TURN_ON_REQUESTED
VALVE_TURN_OFF_REQUESTED
VALVE_TURNED_ON
VALVE_TURNED_OFF

## Sheet3
| TO_TURN_ON_SUCCESS | TURN_ON_REQUESTED | TURN_OFF_REQUESTED | TURNED_ON | TURNED_OFF
CHILLER | FIND_CHILLER_TO_TURN_ON_SUCCESS | CHILLER_TURN_ON_REQUESTED | CHILLER_TURN_OFF_REQUESTED | CHILLER_TURNED_ON | CHILLER_TURNED_OFF
PRIMARY_PUMP | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | PRIMARY_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED | PRIMARY_PUMP_TURNED_ON | PRIMARY_PUMP_TURNED_OFF
PRIMARY_VARIABLE_PUMP | FIND_PRIMARY_VARIABLE_PUMP_TO_TURN_ON_SUCCESS | PRIMARY_VARIABLE_PUMP_TURN_ON_REQUESTED | PRIMARY_VARIABLE_PUMP_TURN_OFF_REQUESTED | PRIMARY_VARIABLE_PUMP_TURNED_ON | PRIMARY_VARIABLE_PUMP_TURNED_OFF
SECONDARY_PUMP | FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS | SECONDARY_PUMP_TURN_ON_REQUESTED | SECONDARY_PUMP_TURN_OFF_REQUESTED | SECONDARY_PUMP_TURNED_ON | SECONDARY_PUMP_TURNED_OFF
CONDENSER_PUMP | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | CONDENSER_PUMP_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_OFF_REQUESTED | CONDENSER_PUMP_TURNED_ON | CONDENSER_PUMP_TURNED_OFF
COOLING_TOWER | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | COOLING_TOWER_TURN_ON_REQUESTED | COOLING_TOWER_TURN_OFF_REQUESTED | COOLING_TOWER_TURNED_ON | COOLING_TOWER_TURNED_OFF
CT_FAN | FIND_CT_FAN_TO_TURN_ON_SUCCESS | CT_FAN_TURN_ON_REQUESTED | CT_FAN_TURN_OFF_REQUESTED | CT_FAN_TURNED_ON | CT_FAN_TURNED_OFF
CT_VARIABLE_FAN | FIND_CT_VARIABLE_FAN_TO_TURN_ON_SUCCESS | CT_VARIABLE_FAN_TURN_ON_REQUESTED | CT_VARIABLE_FAN_TURN_OFF_REQUESTED | CT_VARIABLE_FAN_TURNED_ON | CT_VARIABLE_FAN_TURNED_OFF
HEADER | FIND_HEADER_TO_TURN_ON_SUCCESS | HEADER_TURN_ON_REQUESTED | HEADER_TURN_OFF_REQUESTED | HEADER_TURNED_ON | HEADER_TURNED_OFF
VALVE | FIND_VALVE_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED | VALVE_TURNED_ON | VALVE_TURNED_OFF

## ScenarioTried
| START_STATE | SUCCESS_FORWARD | FAILURE_FORWARD | SUCCESS_RECOVERY
SCENARIO_STARTED | SCENARIO_STARTED | FIND_CHILLER_TO_TURN_ON_SUCCESS | SCENARIO_ABORTED |  | 'SCENARIO_STARTED': {'success': 'FIND_CHILLER_TO_TURN_ON_SUCCESS', 'failure': 'SCENARIO_ABORTED', 'handleFailure': ''},
| FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | VALVE_TURN_ON_REQUESTED | 'FIND_CHILLER_TO_TURN_ON_SUCCESS': {'success': 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'VALVE_TURN_ON_REQUESTED'},
| FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | PRIMARY_PUMP_TURN_ON_REQUESTED | 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS': {'success': 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'PRIMARY_PUMP_TURN_ON_REQUESTED'},
| FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | CONDENSER_PUMP_TURN_ON_REQUESTED | 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS': {'success': 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'CONDENSER_PUMP_TURN_ON_REQUESTED'},
SCENARIO_COMPLETED | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | EQUIPMENT_NOT_AVAILABLE | COOLING_TOWER_TURN_ON_REQUESTED | 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS': {'success': 'VALVE_TURN_ON_REQUESTED', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'COOLING_TOWER_TURN_ON_REQUESTED'},
FIND_CHILLER_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | VALVE_TURNED_ON | VALVE_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'VALVE_TURN_ON_REQUESTED': {'success': 'VALVE_TURNED_ON', 'failure': 'VALVE_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | VALVE_TURNED_ON | PRIMARY_PUMP_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED |  | 'VALVE_TURNED_ON': {'success': 'PRIMARY_PUMP_TURN_ON_REQUESTED', 'failure': 'VALVE_TURN_OFF_REQUESTED', 'handleFailure': ''},
FIND_PRIMARY_VARIABLE_PUMP_TO_TURN_ON_SUCCESS | PRIMARY_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURNED_ON | PRIMARY_PUMP_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'PRIMARY_PUMP_TURN_ON_REQUESTED': {'success': 'PRIMARY_PUMP_TURNED_ON', 'failure': 'PRIMARY_PUMP_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS | PRIMARY_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED |  | 'PRIMARY_PUMP_TURNED_ON': {'success': 'CONDENSER_PUMP_TURN_ON_REQUESTED', 'failure': 'PRIMARY_PUMP_TURN_OFF_REQUESTED', 'handleFailure': ''},
FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | CONDENSER_PUMP_TURN_ON_REQUESTED | CONDENSER_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'CONDENSER_PUMP_TURN_ON_REQUESTED': {'success': 'CONDENSER_PUMP_TURNED_ON', 'failure': 'CONDENSER_PUMP_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | CONDENSER_PUMP_TURNED_ON | COOLING_TOWER_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_OFF_REQUESTED |  | 'CONDENSER_PUMP_TURNED_ON': {'success': 'COOLING_TOWER_TURN_ON_REQUESTED', 'failure': 'CONDENSER_PUMP_TURN_OFF_REQUESTED', 'handleFailure': ''},
FIND_CT_FAN_TO_TURN_ON_SUCCESS | COOLING_TOWER_TURN_ON_REQUESTED | COOLING_TOWER_TURNED_ON | COOLING_TOWER_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'COOLING_TOWER_TURN_ON_REQUESTED': {'success': 'COOLING_TOWER_TURNED_ON', 'failure': 'COOLING_TOWER_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
FIND_CT_VARIABLE_FAN_TO_TURN_ON_SUCCESS | COOLING_TOWER_TURNED_ON | CHILLER_TURN_ON_REQUESTED | COOLING_TOWER_TURN_OFF_REQUESTED |  | 'COOLING_TOWER_TURNED_ON': {'success': 'CHILLER_TURN_ON_REQUESTED', 'failure': 'COOLING_TOWER_TURN_OFF_REQUESTED', 'handleFailure': ''},
FIND_HEADER_TO_TURN_ON_SUCCESS | CHILLER_TURN_ON_REQUESTED | CHILLER_TURNED_ON | CHILLER_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'CHILLER_TURN_ON_REQUESTED': {'success': 'CHILLER_TURNED_ON', 'failure': 'CHILLER_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
CHILLER_TURN_ON_REQUESTED | CHILLER_TURNED_ON | SCENARIO_COMPLETED | CHILLER_TURN_OFF_REQUESTED |  | 'CHILLER_TURNED_ON': {'success': 'SCENARIO_COMPLETED', 'failure': 'CHILLER_TURN_OFF_REQUESTED', 'handleFailure': ''},
PRIMARY_PUMP_TURN_ON_REQUESTED | SCENARIO_COMPLETED |  |  |  | 'SCENARIO_COMPLETED': {'success': '', 'failure': '', 'handleFailure': ''},
PRIMARY_VARIABLE_PUMP_TURN_ON_REQUESTED | EQUIPMENT_NOT_AVAILABLE | SCENARIO_ABORTED |  | SCENARIO_ABORTED | 'EQUIPMENT_NOT_AVAILABLE': {'success': 'SCENARIO_ABORTED', 'failure': '', 'handleFailure': 'SCENARIO_ABORTED'},
SECONDARY_PUMP_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED |  |  | VALVE_TURNED_OFF | 'VALVE_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'VALVE_TURNED_OFF'},
CONDENSER_PUMP_TURN_ON_REQUESTED | VALVE_TURNED_OFF |  |  | FIND_CHILLER_TO_TURN_ON_SUCCESS | 'VALVE_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_CHILLER_TO_TURN_ON_SUCCESS'},
COOLING_TOWER_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED |  |  | PRIMARY_PUMP_TURNED_OFF | 'PRIMARY_PUMP_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'PRIMARY_PUMP_TURNED_OFF'},
CT_FAN_TURN_ON_REQUESTED | PRIMARY_PUMP_TURNED_OFF |  |  | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | 'PRIMARY_PUMP_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS'},
CT_VARIABLE_FAN_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_OFF_REQUESTED |  |  | CONDENSER_PUMP_TURNED_OFF | 'CONDENSER_PUMP_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'CONDENSER_PUMP_TURNED_OFF'},
HEADER_TURN_ON_REQUESTED | CONDENSER_PUMP_TURNED_OFF |  |  | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | 'CONDENSER_PUMP_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS'},
CHILLER_TURN_OFF_REQUESTED | COOLING_TOWER_TURN_OFF_REQUESTED |  |  | COOLING_TOWER_TURNED_OFF | 'COOLING_TOWER_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'COOLING_TOWER_TURNED_OFF'},
PRIMARY_PUMP_TURN_OFF_REQUESTED | COOLING_TOWER_TURNED_OFF |  |  | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | 'COOLING_TOWER_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS'},
PRIMARY_VARIABLE_PUMP_TURN_OFF_REQUESTED | CHILLER_TURN_OFF_REQUESTED |  |  | CHILLER_TURNED_OFF | 'CHILLER_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'CHILLER_TURNED_OFF'},
SECONDARY_PUMP_TURN_OFF_REQUESTED | CHILLER_TURNED_OFF |  |  | FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS | 'CHILLER_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS'},
CONDENSER_PUMP_TURN_OFF_REQUESTED | FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS |  |  | ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED | 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS': {'success': '', 'failure': '', 'handleFailure': 'ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED'},
COOLING_TOWER_TURN_OFF_REQUESTED | ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED |  |  | ALTERNATE_CHILLER_VALVE_TURNED_ON | 'ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'ALTERNATE_CHILLER_VALVE_TURNED_ON'},
CT_FAN_TURN_OFF_REQUESTED | ALTERNATE_CHILLER_VALVE_TURNED_ON |  |  | FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED | 'ALTERNATE_CHILLER_VALVE_TURNED_ON': {'success': '', 'failure': '', 'handleFailure': 'FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED'},
CT_VARIABLE_FAN_TURN_OFF_REQUESTED | FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED |  |  | FIRST_CHILLER_VALVE_TURNED_OFF | 'FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'FIRST_CHILLER_VALVE_TURNED_OFF'},
HEADER_TURN_OFF_REQUESTED | FIRST_CHILLER_VALVE_TURNED_OFF |  |  | DELETE_FIRST_CHILLER_FROM_SCENARIO | 'FIRST_CHILLER_VALVE_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'DELETE_FIRST_CHILLER_FROM_SCENARIO'},
CHILLER_TURNED_ON | DELETE_FIRST_CHILLER_FROM _SCENARIO |  |  | MARK_ALTERNATE_CHILLER_AS_ACTIVE | 'DELETE_FIRST_CHILLER_FROM _SCENARIO': {'success': '', 'failure': '', 'handleFailure': 'MARK_ALTERNATE_CHILLER_AS_ACTIVE'},
PRIMARY_PUMP_TURNED_ON | MARK_CHILLER_AS_FAULTY_IN_SCENARIO |  |  | FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS | 'MARK_CHILLER_AS_FAULTY_IN_SCENARIO': {'success': '', 'failure': '', 'handleFailure': 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS'},
PRIMARY_VARIABLE_PUMP_TURNED_ON | MARK_ALTERNATE_CHILLER_AS_ACTIVE |  |  | CHILLER_TURN_ON_REQUESTED | 'MARK_ALTERNATE_CHILLER_AS_ACTIVE': {'success': '', 'failure': '', 'handleFailure': 'CHILLER_TURN_ON_REQUESTED'},
SECONDARY_PUMP_TURNED_ON | SCENARIO_ABORTED
CONDENSER_PUMP_TURNED_ON
COOLING_TOWER_TURNED_ON
CT_FAN_TURNED_ON
CT_VARIABLE_FAN_TURNED_ON
HEADER_TURNED_ON | VALVE_TURNED_OFF |  | START_CHILLER_SYSTEM
CHILLER_TURNED_OFF | FIND_CHILLER_TO_TURN_ON_SUCCESS
PRIMARY_PUMP_TURNED_OFF
PRIMARY_VARIABLE_PUMP_TURNED_OFF
SECONDARY_PUMP_TURNED_OFF
CONDENSER_PUMP_TURNED_OFF
COOLING_TOWER_TURNED_OFF
CT_FAN_TURNED_OFF
CT_VARIABLE_FAN_TURNED_OFF
HEADER_TURNED_OFF
VALVE_TURN_ON_REQUESTED
VALVE_TURN_OFF_REQUESTED
VALVE_TURNED_ON
VALVE_TURNED_OFF

## Scenario
SCENARIO_NAME | START_STATE | SUCCESS_FORWARD | FAILURE_FORWARD
START_CHILLER_SYSTEM | SCENARIO_STARTED | FIND_CHILLER_TO_TURN_ON_SUCCESS | SCENARIO_ABORTED
| FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | EQUIPMENT_NOT_AVAILABLE
| VALVE_TURN_ON_REQUESTED | VALVE_TURNED_ON | VALVE_TURN_OFF_REQUESTED
| VALVE_TURNED_ON | PRIMARY_PUMP_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED
| PRIMARY_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURNED_ON | PRIMARY_PUMP_TURN_OFF_REQUESTED
PRIMARY_PUMP_TURNED_ON
CONDENSER_PUMP_TURN_ON_REQUESTED
CONDENSER_PUMP_TURNED_ON
COOLING_TOWER_TURN_ON_REQUESTED
COOLING_TOWER_TURNED_ON
CHILLER_TURN_ON_REQUESTED
CHILLER_TURNED_ON
SCENARIO_COMPLETED
EQUIPMENT_NOT_AVAILABLE
| VALVE_TURN_OFF_REQUESTED | VALVE_TURNED_OFF | SCENARIO_NOTIFY_IGNORE
| VALVE_TURNED_OFF | FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_CHILLER_TO_TURN_ON_SUCCESS
| PRIMARY_PUMP_TURN_OFF_REQUESTED | PRIMARY_PUMP_TURNED_OFF | SCENARIO_NOTIFY_IGNORE
| PRIMARY_PUMP_TURNED_OFF | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS
CONDENSER_PUMP_TURN_OFF_REQUESTED
CONDENSER_PUMP_TURNED_OFF
COOLING_TOWER_TURN_OFF_REQUESTED
COOLING_TOWER_TURNED_OFF
CHILLER_TURN_OFF_REQUESTED
CHILLER_TURNED_OFF
START_CHILLER_SYSTEM | SCENARIO_STARTED | FIND_CHILLER_TO_TURN_ON_SUCCESS | SCENARIO_ABORTED
| FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE
| FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | EQUIPMENT_NOT_AVAILABLE
| VALVE_TURN_ON_REQUESTED | VALVE_TURNED_ON | VALVE_TURN_OFF_REQUESTED
| VALVE_TURNED_ON | PRIMARY_PUMP_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED
| PRIMARY_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURNED_ON | PRIMARY_PUMP_TURN_OFF_REQUESTED
| PRIMARY_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED
| CONDENSER_PUMP_TURN_ON_REQUESTED | CONDENSER_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_OFF_REQUESTED
| CONDENSER_PUMP_TURNED_ON | COOLING_TOWER_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_OFF_REQUESTED
| COOLING_TOWER_TURN_ON_REQUESTED | COOLING_TOWER_TURNED_ON | COOLING_TOWER_TURN_OFF_REQUESTED
| COOLING_TOWER_TURNED_ON | CHILLER_TURN_ON_REQUESTED | COOLING_TOWER_TURN_OFF_REQUESTED
| CHILLER_TURN_ON_REQUESTED | CHILLER_TURNED_ON | CHILLER_TURN_OFF_REQUESTED
| CHILLER_TURNED_ON | SCENARIO_COMPLETED
SCENARIO_COMPLETED
| EQUIPMENT_NOT_AVAILABLE | SCENARIO_ABORTED
VALVE_TURN_OFF_REQUESTED
VALVE_TURNED_OFF
PRIMARY_PUMP_TURN_OFF_REQUESTED
PRIMARY_PUMP_TURNED_OFF
CONDENSER_PUMP_TURN_OFF_REQUESTED
CONDENSER_PUMP_TURNED_OFF
| COOLING_TOWER_TURN_OFF_REQUESTED | VALVE_TURNED_OFF
COOLING_TOWER_TURNED_OFF
CHILLER_TURN_OFF_REQUESTED
CHILLER_TURNED_OFF

## Sheet6
START_STATE | SUCCESS_FORWARD | FAILURE_FORWARD | SUCCESS_RECOVERY
ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED |  |  | ALTERNATE_CHILLER_VALVE_TURNED_ON | 'ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'ALTERNATE_CHILLER_VALVE_TURNED_ON'},
ALTERNATE_CHILLER_VALVE_TURNED_ON |  |  | FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED | 'ALTERNATE_CHILLER_VALVE_TURNED_ON': {'success': '', 'failure': '', 'handleFailure': 'FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED'},
CHILLER_TURN_OFF_REQUESTED |  |  | CHILLER_TURNED_OFF | 'CHILLER_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'CHILLER_TURNED_OFF'},
CHILLER_TURN_ON_REQUESTED | CHILLER_TURNED_ON | CHILLER_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'CHILLER_TURN_ON_REQUESTED': {'success': 'CHILLER_TURNED_ON', 'failure': 'CHILLER_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
CHILLER_TURNED_OFF |  |  | FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS | 'CHILLER_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS'},
CHILLER_TURNED_ON | SCENARIO_COMPLETED | CHILLER_TURN_OFF_REQUESTED |  | 'CHILLER_TURNED_ON': {'success': 'SCENARIO_COMPLETED', 'failure': 'CHILLER_TURN_OFF_REQUESTED', 'handleFailure': ''},
CONDENSER_PUMP_TURN_OFF_REQUESTED |  |  | CONDENSER_PUMP_TURNED_OFF | 'CONDENSER_PUMP_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'CONDENSER_PUMP_TURNED_OFF'},
CONDENSER_PUMP_TURN_ON_REQUESTED | CONDENSER_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'CONDENSER_PUMP_TURN_ON_REQUESTED': {'success': 'CONDENSER_PUMP_TURNED_ON', 'failure': 'CONDENSER_PUMP_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
CONDENSER_PUMP_TURNED_OFF |  |  | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | 'CONDENSER_PUMP_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS'},
CONDENSER_PUMP_TURNED_ON | COOLING_TOWER_TURN_ON_REQUESTED | CONDENSER_PUMP_TURN_OFF_REQUESTED |  | 'CONDENSER_PUMP_TURNED_ON': {'success': 'COOLING_TOWER_TURN_ON_REQUESTED', 'failure': 'CONDENSER_PUMP_TURN_OFF_REQUESTED', 'handleFailure': ''},
COOLING_TOWER_TURN_OFF_REQUESTED |  |  | COOLING_TOWER_TURNED_OFF | 'COOLING_TOWER_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'COOLING_TOWER_TURNED_OFF'},
COOLING_TOWER_TURN_ON_REQUESTED | COOLING_TOWER_TURNED_ON | COOLING_TOWER_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'COOLING_TOWER_TURN_ON_REQUESTED': {'success': 'COOLING_TOWER_TURNED_ON', 'failure': 'COOLING_TOWER_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
COOLING_TOWER_TURNED_OFF |  |  | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | 'COOLING_TOWER_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS'},
COOLING_TOWER_TURNED_ON | CHILLER_TURN_ON_REQUESTED | COOLING_TOWER_TURN_OFF_REQUESTED |  | 'COOLING_TOWER_TURNED_ON': {'success': 'CHILLER_TURN_ON_REQUESTED', 'failure': 'COOLING_TOWER_TURN_OFF_REQUESTED', 'handleFailure': ''},
DELETE_FIRST_CHILLER_FROM _SCENARIO |  |  | MARK_ALTERNATE_CHILLER_AS_ACTIVE | 'DELETE_FIRST_CHILLER_FROM _SCENARIO': {'success': '', 'failure': '', 'handleFailure': 'MARK_ALTERNATE_CHILLER_AS_ACTIVE'},
EQUIPMENT_NOT_AVAILABLE | SCENARIO_ABORTED |  | SCENARIO_ABORTED | 'EQUIPMENT_NOT_AVAILABLE': {'success': 'SCENARIO_ABORTED', 'failure': '', 'handleFailure': 'SCENARIO_ABORTED'},
FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS |  |  | ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED | 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS': {'success': '', 'failure': '', 'handleFailure': 'ALTERNATE_CHILLER_VALVE_TURN_ON_REQUESTED'},
FIND_CHILLER_TO_TURN_ON_SUCCESS | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | VALVE_TURN_ON_REQUESTED | 'FIND_CHILLER_TO_TURN_ON_SUCCESS': {'success': 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'VALVE_TURN_ON_REQUESTED'},
FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | CONDENSER_PUMP_TURN_ON_REQUESTED | 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS': {'success': 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'CONDENSER_PUMP_TURN_ON_REQUESTED'},
FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS | VALVE_TURN_ON_REQUESTED | EQUIPMENT_NOT_AVAILABLE | COOLING_TOWER_TURN_ON_REQUESTED | 'FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS': {'success': 'VALVE_TURN_ON_REQUESTED', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'COOLING_TOWER_TURN_ON_REQUESTED'},
FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS | EQUIPMENT_NOT_AVAILABLE | PRIMARY_PUMP_TURN_ON_REQUESTED | 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS': {'success': 'FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS', 'failure': 'EQUIPMENT_NOT_AVAILABLE', 'handleFailure': 'PRIMARY_PUMP_TURN_ON_REQUESTED'},
FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED |  |  | FIRST_CHILLER_VALVE_TURNED_OFF | 'FIRST_CHILLER_VALVE_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'FIRST_CHILLER_VALVE_TURNED_OFF'},
FIRST_CHILLER_VALVE_TURNED_OFF |  |  | DELETE_FIRST_CHILLER_FROM_SCENARIO | 'FIRST_CHILLER_VALVE_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'DELETE_FIRST_CHILLER_FROM_SCENARIO'},
MARK_ALTERNATE_CHILLER_AS_ACTIVE |  |  | CHILLER_TURN_ON_REQUESTED | 'MARK_ALTERNATE_CHILLER_AS_ACTIVE': {'success': '', 'failure': '', 'handleFailure': 'CHILLER_TURN_ON_REQUESTED'},
MARK_CHILLER_AS_FAULTY_IN_SCENARIO |  |  | FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS | 'MARK_CHILLER_AS_FAULTY_IN_SCENARIO': {'success': '', 'failure': '', 'handleFailure': 'FIND_ALTERNATE_CHILLER_TO_TURN_ON_SUCCESS'},
PRIMARY_PUMP_TURN_OFF_REQUESTED |  |  | PRIMARY_PUMP_TURNED_OFF | 'PRIMARY_PUMP_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'PRIMARY_PUMP_TURNED_OFF'},
PRIMARY_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURNED_ON | PRIMARY_PUMP_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'PRIMARY_PUMP_TURN_ON_REQUESTED': {'success': 'PRIMARY_PUMP_TURNED_ON', 'failure': 'PRIMARY_PUMP_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
PRIMARY_PUMP_TURNED_OFF |  |  | FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS | 'PRIMARY_PUMP_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS'},
PRIMARY_PUMP_TURNED_ON | CONDENSER_PUMP_TURN_ON_REQUESTED | PRIMARY_PUMP_TURN_OFF_REQUESTED |  | 'PRIMARY_PUMP_TURNED_ON': {'success': 'CONDENSER_PUMP_TURN_ON_REQUESTED', 'failure': 'PRIMARY_PUMP_TURN_OFF_REQUESTED', 'handleFailure': ''},
SCENARIO_ABORTED |  |  |  | 'SCENARIO_ABORTED': {'success': '', 'failure': '', 'handleFailure': ''},
SCENARIO_COMPLETED |  |  |  | 'SCENARIO_COMPLETED': {'success': '', 'failure': '', 'handleFailure': ''},
SCENARIO_STARTED | FIND_CHILLER_TO_TURN_ON_SUCCESS | SCENARIO_ABORTED |  | 'SCENARIO_STARTED': {'success': 'FIND_CHILLER_TO_TURN_ON_SUCCESS', 'failure': 'SCENARIO_ABORTED', 'handleFailure': ''},
VALVE_TURN_OFF_REQUESTED |  |  | VALVE_TURNED_OFF | 'VALVE_TURN_OFF_REQUESTED': {'success': '', 'failure': '', 'handleFailure': 'VALVE_TURNED_OFF'},
VALVE_TURN_ON_REQUESTED | VALVE_TURNED_ON | VALVE_TURN_OFF_REQUESTED | SCENARIO_RECOVERED | 'VALVE_TURN_ON_REQUESTED': {'success': 'VALVE_TURNED_ON', 'failure': 'VALVE_TURN_OFF_REQUESTED', 'handleFailure': 'SCENARIO_RECOVERED'},
VALVE_TURNED_OFF |  |  | FIND_CHILLER_TO_TURN_ON_SUCCESS | 'VALVE_TURNED_OFF': {'success': '', 'failure': '', 'handleFailure': 'FIND_CHILLER_TO_TURN_ON_SUCCESS'},
VALVE_TURNED_ON | PRIMARY_PUMP_TURN_ON_REQUESTED | VALVE_TURN_OFF_REQUESTED |  | 'VALVE_TURNED_ON': {'success': 'PRIMARY_PUMP_TURN_ON_REQUESTED', 'failure': 'VALVE_TURN_OFF_REQUESTED', 'handleFailure': ''},
"SET_VALIDATE_PROCESS_PARAMS_ON": { "EQUIPMENT_TYPE": "NONGL_SS_HEADER", "Eqp_Attributes": { "CWH_ST": 7 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "Monitor" },
"FIND_CHILLER_TO_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_SS": 0, "CH_Trip_SS": 0, "CH_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"VALVE_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_Vlv_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"VALVE_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_Vlv_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"CONDENSER_VALVE_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CD_In_Vlv_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"CONDENSER_VALVE_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CD_In_Vlv_On_Off_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"CONDENSER_VALVE_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CD_In_Vlv_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"CONDENSER_VALVE_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CD_In_Vlv_On_Off_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"CHILLER_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"CHILLER_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"CHILLER_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"CHILLER_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_PRIMARY_PUMP_TO_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_SS": 0, "Pri_Pmp_Trip_SS": 0, "Pri_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"PRIMARY_PUMP_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"PRIMARY_PUMP_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"CHECK_CHILLER_WATER_FLOW_STATUS": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CHW_Flow_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_CONDENSER_PUMP_TO_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_SS": 0, "Cnd_Pmp_Trip_SS": 0, "Cnd_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"CONDENSER_PUMP_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"CONDENSER_PUMP_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"CHECK_CONDENSER_WATER_FLOW_STATUS": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CHW_Flow_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_COOLING_TOWER_TO_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CTW_Low_Lvl": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false },
"EQP_COMPONENTS": [ { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_AM_SS": 1, "CT_Fan_Run_SS": 0, "CT_Fan_Trip_SS": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false } } ], "ACTION_REQUIRED": "find_update" },
"COOLING_TOWER_VALVE_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CT_Out_Vlv_On_Off_Cmd": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "bacnet_write" },
"COOLING_TOWER_VALVE_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CT_Out_Vlv_On_Off_Fbk": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_COOLING_TOWER_FAN_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_AM_SS": 1, "CT_Fan_Run_SS": 0, "CT_Fan_Trip_SS": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"COOLING_TOWER_FAN_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_On_Off_Cmd": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"COOLING_TOWER_FAN_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_On_Off_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_SECONDARY_PUMP_TO_TURNED_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_SECONDARY_PUMP", "Eqp_Attributes": { "Sec_Pmp_SS": 0, "Sec_Pmp_Trip_SS": 0, "Sec_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"SECONDARY_PUMP_TURN_ON_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_SECONDARY_PUMP", "Eqp_Attributes": { "Sec_Pmp_On_Off": 1 }, "ACTION_REQUIRED": "bacnet_write" },
"SECONDARY_PUMP_TURNED_ON": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "Sec_Pmp_SS": 1 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_CHILLER_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_SS": 1, "CH_Trip_SS": 0, "CH_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"VALVE_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_Vlv_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"VALVE_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_Vlv_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_PRIMARY_PUMP_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_SS": 1, "Pri_Pmp_Trip_SS": 0, "Pri_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"PRIMARY_PUMP_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"PRIMARY_PUMP_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_SS": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"FIND_CONDENSER_PUMP_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_SS": 1, "Cnd_Pmp_Trip_SS": 0, "Cnd_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"CONDENSER_PUMP_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"CONDENSER_PUMP_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_COOLING_TOWER_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CTW_Low_Lvl": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false },
"EQP_COMPONENTS": [ { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_AM_SS": 1, "CT_Fan_Run_SS": 0, "CT_Fan_Trip_SS": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false } } ], "ACTION_REQUIRED": "find_update" },
"COOLING_TOWER_VALVE_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CT_Out_Vlv_On_Off_Cmd": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "bacnet_write" },
"COOLING_TOWER_VALVE_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CT_Out_Vlv_On_Off_Fbk": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_COOLING_TOWER_FAN_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_AM_SS": 1, "CT_Fan_Run_SS": 1, "CT_Fan_Trip_SS": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"COOLING_TOWER_FAN_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_On_Off_Cmd": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"COOLING_TOWER_FAN_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CT_FAN", "Eqp_Attributes": { "CT_Fan_On_Off_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_SECONDARY_PUMP_TO_TURNED_OFF_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_SECONDARY_PUMP", "Eqp_Attributes": { "Sec_Pmp_SS": 1, "Sec_Pmp_Trip_SS": 0, "Sec_Pmp_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"SECONDARY_PUMP_TURN_OFF_REQUESTED": { "EQUIPMENT_TYPE": "NONGL_SS_SECONDARY_PUMP", "Eqp_Attributes": { "Sec_Pmp_On_Off": 0 }, "ACTION_REQUIRED": "bacnet_write" },
"SECONDARY_PUMP_TURNED_OFF": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "Sec_Pmp_SS": 0 }, "ACTION_REQUIRED": "snapshot_check" },
"FIND_CHILLER_TO_TURN_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CHILLER", "Eqp_Attributes": { "CH_SS": 0, "CH_Trip_SS": 0, "CH_AM_SS": 1 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "ACTION_REQUIRED": "find_update" },
"FIND_PRIMARY_PUMP_TO_TURN_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_PRIMARY_PUMP", "Eqp_Attributes": { "Pri_Pmp_On_Off": 0 }, "ACTION_REQUIRED": "find_update" },
"FIND_CONDENSER_PUMP_TO_TURN_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_CONDENSER_PUMP", "Eqp_Attributes": { "Cnd_Pmp_On_Off": 0 }, "ACTION_REQUIRED": "find_update" },
"FIND_SECONDARY_PUMP_TO_TURN_ON_SUCCESS": {},
"FIND_COOLING_TOWER_TO_TURN_ON_SUCCESS": { "EQUIPMENT_TYPE": "NONGL_SS_COOLING_TOWER", "Eqp_Attributes": { "CTW_Low_Lvl": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false }, "EQP_COMPONENTS": { "NONGL_SS_CT_FAN": { "Eqp_Attributes": { "CT_Fan_AM_SS": 1, "CT_Fan_On_Off_SS": 0, "CT_Fan_Trip_SS": 0 }, "Eqp_Metrics": { "Run_Hours": "LEAST", "Equipment_Faulty": false } } }, "ACTION_REQUIRED": "find_update" }